## System Parameters
SYSTEM PARAMETERS
| A. | Airport Name
| B. | Circuit Identification (if applicable)
| C. | Maximum CCR Output Current |  | Amps |  | Select from dropdown or type-in
| D. | Number of CCR Steps |  |  |  | Select from dropdown or type-in
| E. | Input Voltage |  |  |  | Select from dropdown or type-in
| F. | Frequency |  |  |  | Select from dropdown
| G. | Series Circuit Cable Wire Length Units | Feet |  |  | Select from dropdown or type-in
| H. | CCR Architecture |  |  |  | Select from dropdown or type-in
| I. | Estimated roundtrip length of L-824 series circuit wire |  |  | Feet
| J. | L-824 Wire Size |  | AWG
| K. | L-824 Wire Resistance |  | ohms/1,000 Feet
Note:
|  | For Tamaqua AWG 6, use 0.42 ohms/1,000 Feet |  | L-824 LOAD | 0 |  | VA
For Tamaqua AWG 8, use 0.66 ohms/1,000 Feet
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Lamp Load
Tungsten Halogen/Incandescent Lamp Load
| 1. | Fixture Load Calculator #1
|  | A. | Fixture Description |  | L-850A |  | Select from dropdown or type-in
|  | B. | Manufacturer | [6 empty] | Select from dropdown or type-in
|  | C. | Number of Light Fixtures
|  | D. | Lamp Wattage* |  |  | W |  |  |  |  | * | Note: If fixture has multiple lamps, enter maximum wattage when maximum number of lamps are on. Example: For a bi-directional L-852D (with two 30W lamps) where both lamps can be on at the same time, enter 60W.
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG |  | Select from dropdown or type-in
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer** |  |  | VA |  |  |  |  | ** | Note: Any other load not listed in calculator.
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total CCR Load for Fixture No. 1 |  |  |  |  | 0 | VA
| 2. | Fixture Load Calculator #2
|  | A. | Fixture Description |  |  |  | Select from dropdown or type-in
|  | B. | Manufacturer | [6 empty] | Select from dropdown or type-in
|  | C. | Number of Light Fixtures
|  | D. | Lamp Wattage* |  |  | W |  |  |  |  | * | Note: If fixture has multiple lamps, enter maximum wattage when maximum number of lamps are on. Example: For a bi-directional L-852D (with two 30W lamps) where both lamps can be on at the same time, enter 60W.
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG |  | Select from dropdown or type-in
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer** |  |  | VA |  |  |  |  | ** | Note: Any other load not listed in calculator.
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 2 |  |  |  |  | 0 | VA
| 3. | Fixture Load Calculator #3
|  | A. | Fixture Description |  |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | Lamp Wattage* |  |  | W |  |  |  |  | * | Note: If fixture has multiple lamps, enter maximum wattage when maximum number of lamps are on. Example: For a bi-directional L-852D (with two 30W lamps) where both lamps can be on at the same time, enter 60W.
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG |  | Select from dropdown or type-in
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer** |  |  | VA |  |  |  |  | ** | Note: Any other load not listed in calculator.
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 3 |  |  |  |  | 0 | VA
| 4. | Fixture Load Calculator #4
|  | A. | Fixture Description |  |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | Lamp Wattage* |  |  | W |  |  |  |  | * | Note: If fixture has multiple lamps, enter maximum wattage when maximum number of lamps are on. Example: For a bi-directional L-852D (with two 30W lamps) where both lamps can be on at the same time, enter 60W.
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG |  | Select from dropdown or type-in
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer** |  |  | VA |  |  |  |  | ** | Note: Any other load not listed in calculator.
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 4 |  |  |  |  | 0 | VA
|  | Total Tungsten-Halogen/Incandescent Lamp Load | [6 empty] | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## LED Load
LED LOAD
Note: Use tab "Other Load(s)" to enter LED PAPI, REIL and Wind Cone data. If using LED Signs or
elevated/in-pavement Runway Guard Lights use those tabs to enter data.
| 1. | Fixture Load Calculator #1
|  | A. | Fixture Description |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | LED fixture load |  |  | VA
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer * |  |  | VA
(Any other load not listed in calculator.)
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 1 |  |  |  |  | 0 | VA
| 2. | Fixture Load Calculator #2
|  | A. | Fixture Description |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | LED fixture load |  |  | VA
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer |  |  | VA
(Any other load not listed in calculator.)
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 2 |  |  |  |  | 0 | VA
| 3. | Fixture Load Calculator #3
|  | A. | Fixture Description |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | LED fixture load |  |  | VA
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer |  |  | VA
(Any other load not listed in calculator.)
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 3 |  |  |  |  | 0 | VA
| 4. | Fixture Load Calculator #4
|  | A. | Fixture Description |  |  | Select from dropdown or type-in
|  | B. | Manufacturer
|  | C. | Number of Light Fixtures
|  | D. | LED fixture load |  |  | VA
|  | E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  |  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  |  | Feet
|  |  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  |  | AWG
|  |  | 3. Wire Resistance | 0 | ohms / 1000 Feet |  | 0 | VA
|  | F. | Other Load on Isolation Transformer |  |  | VA
(Any other load not listed in calculator.)
|  | G. | Total Isolation Transformer Load |  | 0 | VA
|  | H. | Isolation Transformer Used |  |  | W
|  | I. | Isolation Transformer Losses |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
|  |  |  | Total Fixture Load No. 4 |  |  |  |  | 0 | VA
|  | Total LED Fixture Load |  | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Sign Load
FAA L-858 / ICAO / TP312 Sign Load
| 1. | Sign Load No. 1 Calculator | [5 empty] | Reference Data:
|  | A. | Sign Manufacturer | Dropdown or type-in
|  | B. | Sign Size |  |  |  |  | FAA Sign Sizes
|  | C. | Number of Sign Modules |  |  |  |  | Size 1 means 12 in. (30.5 cm) Legend Height
|  | Note: Enter sign length for ICAO/TP312 signs. | [5 empty] | Size 2 means 15 in (38.1 cm) Legend Height
|  | D. | Light Source | Dropdown or type-in |  |  |  | Size 3 means 18 in (45.7 cm) Legend Height
|  | E. | Sign Power Architecture | also type-in |  |  |  | Size 4 means 40 in (101.6 cm) Legend Height
|  | F. | Sign Style |  |  |  |  | Size 5 means 25 in (63.5 cm) Legend Height
|  | G. | Sign Transformer Used |  |  |  | W | FAA Sign Types
|  | H. | Sign VA as seen on the primary of the isolation transformer |  |  |  | VA | Type | Legend Color | Background Color
[5 empty] | Autofill or type-in |  |  | L-858Y | Black | Yellow
|  | I. | Total Number of Signs in this Configuration |  |  |  |  | L-858R | White with Black Outline | Red
[8 empty] | L-858L | Yellow | Black
|  |  | Total Sign Load No. 1 | 0 | VA |  |  | L-858B | White | Black
| 2. | Sign Load No. 2 Calculator
|  | A. | Sign Manufacturer | Dropdown or type-in
|  | B. | Sign Size
|  | C. | Number of Sign Modules
Note: Enter sign length for ICAO/TP312 signs.
|  | D. | Light Source | Dropdown or type-in
|  | E. | Sign Power Architecture | also type-in
|  | F. | Sign Style
|  | G. | Sign Transformer Used |  |  |  | W
|  | H. | Sign VA as seen on the primary of the isolation transformer |  |  |  | VA
Autofill or type-in
|  | I. | Total Number of Signs in this Configuration
|  |  | Total Sign Load No. 2 | 0 | VA
| 3. | Sign Load No. 3 Calculator
|  | A. | Sign Manufacturer | Dropdown or type-in
|  | B. | Sign Size
|  | C. | Number of Sign Modules
Note: Enter sign length for ICAO/TP312 signs.
|  | D. | Light Source | Dropdown or type-in
|  | E. | Sign Power Architecture | also type-in
|  | F. | Sign Style
|  | G. | Sign Transformer Used |  |  |  | W
|  | H. | Sign VA as seen on the primary of the isolation transformer |  |  |  | VA
Autofill or type-in
|  | I. | Total Number of Signs in this Configuration
|  |  | Total Sign Load No. 3 | 0 | VA
| 4. | Sign Load No. 4 Calculator
|  | A. | Sign Manufacturer | Dropdown or type-in
|  | B. | Sign Size
|  | C. | Number of Sign Modules
Note: Enter sign length for ICAO/TP312 signs.
|  | D. | Light Source | Dropdown or type-in
|  | E. | Sign Power Architecture | also type-in
|  | F. | Sign Style
|  | G. | Sign Transformer Used |  |  |  | W
|  | H. | Sign VA as seen on the primary of the isolation transformer |  |  |  | VA
Autofill or type-in
|  | I. | Total Number of Signs in this Configuration
|  |  | Total Sign Load No. 4 | 0 | VA
| 5. | Sign Load No. 5 Calculator
|  | A. | Sign Manufacturer | Dropdown or type-in
|  | B. | Sign Size
|  | C. | Number of Sign Modules
Note: Enter sign length for ICAO/TGP312 signs.
|  | D. | Light Source | Dropdown or type-in
|  | E. | Sign Power Architecture | also type-in
|  | F. | Sign Style
|  | G. | Sign Transformer Used |  |  |  | W
|  | H. | Sign VA as seen on the primary of the isolation transformer |  |  |  | VA
Autofill or type-in
|  | I. | Total Number of Signs in this Configuration
|  |  | Total Sign Load No. 5 | 0 | VA
|  | Total Sign Load |  |  |  | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## In-pavement RGL
In-Pavement Runway Guard Light (RGL)
In-pavement RGL Load Calculator
| A. | Fixture Description | L-852G
Note: Use the Stop Bar tab if the fixture is a L-852G/S.
| B. | Fixture Manufacturer |  | Select from dropdown or type-in
| C. | Fixture Load |  | W or VA (LED) |  | Select from dropdown or type-in
| D. | Monitored or Unmonitored?
Note: Selecting Unmonitored zeros out any load associated with the Master.
| E. | Isolation Transformer Wattage |  | W | Select from dropdown or type-in
| F. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  | Feet
|  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  | AWG
|  | 3. Wire Resistance | ohms / 1000 Feet |  | 0 | VA
| G. | Type of Fixture Pulsing Device Used |  |  |  |  | Select from dropdown or type-in
|  | 1. Other Pulsing Device Load plus isolation transformer loss when ON |  |  |  |  | VA | *Note: Enter isolation transformer load if LED.
|  | 2. Other Pulsing Device Load plus isolation transformer loss when OFF |  |  |  |  | VA | *Note: Used for incandescent only. Enter 0 if LED.
| H. | Total Number of In-pavement Light Fixtures on Circuit
Note: The load calculations assumes the fixtures alternately pulse according to FAA requirements.
| I. | Any Other Load on CCR |  | VA
| J. | Monitoring Device Load (if present). | 0 | VA
Note: This, for example, is the BRITE/AGLAS Master load, if any.
Note: This calculation assumes that there is no operational need to have all lights ON at the same time. If all the lights are ON, the CCR might be overloaded in at least the high step (B5/B100). The FAA requires that RGLs pulse in all operational modes: Power-on, Normal Operation, and Failsafe mode. Therefore, there is no operational situation in which RGL lights will be steady burning ON.
There also might be a CCR loading consideration if pulsing RGLs are being phased in with existing steady-burning yellow hold bars and all lights will be steady-burning initially.
Load Calculation
[7 empty] | Max. CCR Load for Fixture + Pulsing Device + Transformer |  | 0 | VA
[7 empty] | Monitoring Device Load + Other Load |  | 0 | VA
[7 empty] | Total In-pavement RGL Fixture load |  | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Elevated RGL
Elevated L-804 Runway Guard Light (RGL)
| A. | Fixture Description | L-804
Note: Use the Stop Bar tab if the L-804 is on the same circuit as the Stop Bar.
| B. | Fixture Manufacturer |  | Select from dropdown or type-in
| C. | Fixture Load |  | W or VA (LED) |  | Select from dropdown or type-in
Note: Enter the wattage for only one of the two lamps in the L-804 (since only one is on at a time.)
| D. | Type of Fixture Pulsing Device Used |  | Select from dropdown or type-in
Note: Entering PCB version inserts load for PCB only and auto zeros anything associated with BRITE / AGLAS
|  | 1. Pulsing Device Load. |  |  | 0 | VA |  | *Note: Enter 0 if LED.
| E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of Isolation Transformer secondary wire |  |  |  | Feet
|  | 2. Isolation Transformer Secondary Wire Gauge |  |  |  | AWG
|  | 3. Wire Resistance | ohms / 1000 Feet |  | 0 | VA
| F. | Total Isolation Transformer Load | 0 | VA
| G. | Isolation Transformer Wattage |  | W | Select from dropdown or type-in
|  | Isolation Transformer Losses | 0 | VA | * Note: Value will autofill, but you can manually enter a number
| H. | Total Number of Elevated Light Fixtures on Circuit
Note: The load calculations assumes the fixtures alternately pulse according to FAA requirements.
| I. | Any Other Load on CCR |  | VA
| J. | Monitored or Unmonitored?
Note: Selecting Unmonitored zeros out any load associated with the Master.
| K. | Monitoring Device Load (if present). | 0 | VA | Type-in
Note: This, for example, is the BRITE/AGLAS Master load, if any.
Load Calculation
[7 empty] | Max. CCR Load for Fixture + Pulsing Device + Transformer Losses |  | 0 | VA
[7 empty] | Monitoring Device Load + Other Load |  | 0 | VA
[7 empty] | Total Elevated RGL Fixture Load |  | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Stop Bar
Stop Bar Loads, with or without In-pavement & Elevated RGL Loads
In-pavement Stop Bar
| A. | Fixture Description |  |  |  |  | Note: Typing in L-852G/S enables all L-852G rows.
| B. | Fixture Manufacturer
| C. | Fixture Load |  |  |  | W or VA (LED)
| D. | Type of Control/Monitoring Device Used
|  | 1. Max. Control/Monitoring Device Load |  |  |  | VA
| E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of L-830 secondary wire |  |  |  | Feet
2. L-830 Secondary Wire Gauge
|  | 3. Wire Resistance | 0 | ohms / 1000 Feet | 0 | Load
| F. | Isolation Transformer Wattage |  |  |  | W
| G. | Isolation Transformer Losses |  |  | 0
| H. | Total Individual Fixture CCR Load |  |  | 0 |  |  | SubTotal
| I. | Total Number of In-pavement Stop Bar Fixtures on Circuit | [5 empty] | 0
Load Calculation
Elevated Stop Bar
[9 empty] | Total Stop Bar Load | VA
| A. | Fixture Description
| B. | Fixture Manufacturer
| C. | Fixture Load |  |  |  | W or VA (LED)
| D. | Type of Control/Monitoring Device Used
|  | 1. Max. Control/Monitoring Device Load |  |  |  | VA
| E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of L-830 secondary wire |  |  |  | Feet
2. L-830 Secondary Wire Gauge
|  | 3. Wire Resistance | 0 | ohms / 1000 Feet | 0 | Load
| F. | Isolation Transformer Wattage |  |  |  | W
| G. | Isolation Transformer Losses |  |  | 0
| H. | Total Individual Fixture CCR Load |  |  | 0 |  |  | SubTotal
| I. | Total Number of Elevated Stop Bar Fixtures on Circuit | [5 empty] | 0
Load Calculation
Sensor Load
[9 empty] | Total Stop Bar Load | VA
| A. | Type of Sensor Used
| B. | Individual Sensor + Isolation Transformer (if present) Load |  |  |  | VA |  | SubTotal
| C. | Total number of sensors | [5 empty] | 0
| In-pavement RGL Load Calculator (L-852G Side only in RVR >1200 ft.) | [7 empty] | Total Sensor Load | VA
| A. | Fixture Description |  |  | L-852G
| B. | Fixture Manufacturer
| C. | Fixture Load |  |  |  | W or VA (LED)
| D. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of L-830 secondary wire |  |  |  | Feet
2. L-830 Secondary Wire Gauge
|  | 3. Wire Resistance | 0 | ohms / 1000 Feet | 0 | Load
| E. | Isolation Transformer Wattage |  |  |  | W
| F. | Type of Fixture Pulsing Device Used
|  | 1. Other Pulsing Device Load plus isolation transformer loss when ON |  |  |  | VA | *Note: Enter isolation transformer load if LED.
|  | 2. Other Pulsing Device Load plus isolation transformer loss when OFF |  |  |  | VA | *Note: Used for incandescent only. Enter 0 if LED.
SubTotal
| G. | Total Number of In-pavement Light Fixtures on Circuit | [5 empty] | 0
Note: The load calculations assumes the fixtures alternately pulse according to FAA requirements.
Note: This calculation assumes that there is no operational need to have all lights ON at the same time. If all the lights are ON, the CCR might be overloaded in at least the high step (B5/B100). The FAA requires that RGLs pulse in all operational modes: Power-on, Normal Operation, and Failsafe mode. Therefore, there is no operational situation in which RGL lights will be steady burning ON.
Elevated L-804 Runway Guard Light (RGL)
| A. | Fixture Description |  |  | L-804
Note: Use this Stop Bar tab if the L-804 is on the same circuit as the Stop Bar.
| B. | Fixture Manufacturer
| C. | Fixture Load |  |  |  | W or VA (LED)
Note: Enter the wattage for only one of the two lamps in the L-804 (since only one is on at a time.)
| D. | Type of Fixture Pulsing Device Used
Note: Entering PCB version inserts load for PCB only and auto zeros anything associated with BRITE / AGLAS
|  | 1. Pulsing Device Load. |  |  | 0 | VA | *Note: Enter 0 if LED.
| E. | Are long secondary wires present?
Note: Zero is automatically assumed if transformer is located underneath fixture.
|  | 1. Estimated roundtrip length of L-830 secondary wire |  |  |  | Feet
2. L-830 Secondary Wire Gauge
|  | 3. Wire Resistance | 0 | ohms / 1000 Feet | 0 | Load
| F. | Isolation Transformer Wattage |  |  |  | W
| G. | Isolation Transformer Losses |  |  | 0 | VA | * Note: Value will autofill, but you can manually enter a number
| H. | Max CCR Load for Fixture + Pulsing Device + Transformer |  |  | 0 | VA |  | SubTotal
| I. | Total Number of Elevated Light Fixtures on Circuit | [5 empty] | 0
Note: The load calculations assumes the fixtures alternately pulse according to FAA requirements.
Control/Monitoring Interface Device Load
| A. | Monitoring Device Load (if present). |  |  | 0 | VA
|  | Note: This, for example, is the BRITE/AGLAS Master load, if any. | [5 empty] | SubTotal
| B. | Any Other Load |  |  |  | VA |  | 0
Total Stop Bar Load
0
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Other Load(s)
Other Load(s)
|  | 1. | Other Load Description (Select From Dropdown or Type-in) |  |  | 2. | Other Load Description (Select From Dropdown or Type-in)
|  |  | Device VA |  | VA |  | Device VA |  | VA
|  |  | Isolation Transformer Used (if any) |  |  |  | Isolation Transformer Used (if any)
|  |  | Isolation Transformer Losses (if any) | 0 |  |  | Isolation Transformer Losses (if any) | 0
|  |  | Other Losses (if any) |  |  |  | Other Losses (if any)
|  |  | Quantity |  |  |  | Quantity
|  |  | Total Load | 0 | VA |  | Total Load | 0 | VA | 0
|  | 3. | Other Load Description (Select From Dropdown or Type-in) |  |  | 4. | Other Load Description (Select From Dropdown or Type-in)
|  |  | Device VA |  | VA |  | Device VA |  | VA
|  |  | Isolation Transformer Used (if any) |  |  |  | Isolation Transformer Used (if any)
|  |  | Isolation Transformer Losses (if any) | 0 |  |  | Isolation Transformer Losses (if any) | 0
|  |  | Other Losses (if any) |  |  |  | Other Losses (if any)
|  |  | Quantity |  |  |  | Quantity
|  |  | Total Load | 0 | VA |  | Total Load | 0 | VA
|  | 5. | Other Load Description (Select From Dropdown or Type-in) |  |  | 6. | Other Load Description (Select From Dropdown or Type-in)
|  |  | Device VA |  | VA |  | Device VA |  | VA
|  |  | Isolation Transformer Used (if any) |  |  |  | Isolation Transformer Used (if any)
|  |  | Isolation Transformer Losses (if any) |  |  |  | Isolation Transformer Losses (if any)
|  |  | Other Losses (if any) |  |  |  | Other Losses (if any)
|  |  | Quantity |  |  |  | Quantity
|  |  | Total Load | 0 | VA |  | Total Load | 0 | VA | 0
|  | 7. | Other Load Description (Select From Dropdown or Type-in) |  |  | 8. | Other Load Description (Select From Dropdown or Type-in)
|  |  | Device VA |  | VA |  | Device VA |  | VA
|  |  | Isolation Transformer Used (if any) |  |  |  | Isolation Transformer Used (if any)
|  |  | Isolation Transformer Losses (if any) | 0 |  |  | Isolation Transformer Losses (if any) | 0
|  |  | Other Losses (if any) |  |  |  | Other Losses (if any)
|  |  | Quantity |  |  |  | Quantity
|  |  | Total Load | 0 | VA |  | Total Load | 0 | VA
|  | 9. | Other Load Description (Select From Dropdown or Type-in) |  |  | 10. | Other Load Description (Select From Dropdown or Type-in)
|  |  | Device VA |  | VA |  | Device VA |  | VA
|  |  | Isolation Transformer Used (if any) |  |  |  | Isolation Transformer Used (if any)
|  |  | Isolation Transformer Losses (if any) | 0 |  |  | Isolation Transformer Losses (if any) | 0
|  |  | Other Losses (if any) |  |  |  | Other Losses (if any)
|  |  | Quantity |  |  |  | Quantity
|  |  | Total Load | 0 | VA |  | Total Load | 0 | VA
| Total Other Loads | [6 empty] | 0 | VA
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## Load Summary
CCR Load Summary
Airport Name
Circuit Identification
Maximum CCR Output Current
Number of CCR Steps
Input Voltage
Frequency
CCR Architecture
Load Description | Device Description |  |  | Manuf. | Isolation Transformer Used | Qty. | Individual Device CCR Load VA | Subtotal Load VA | Subtotal Load Type VA
Lamp Load 1 | L-850A |  |  |  | W | 0 | 0 | 0
Lamp Load 2 |  |  |  |  | W | 0 | 0 | 0
Lamp Load 3 |  |  |  |  | W | 0 | 0 | 0
Lamp Load 4 |  |  |  |  | W | 0 | 0 | 0
Total Lamp Load | [8 empty] | 0
LED Load 1 |  |  |  |  | W | 0 | 0 | 0
LED Load 2 |  |  |  |  | W | 0 | 0 | 0
LED Load 3 |  |  |  |  | W | 0 | 0 | 0
LED Load 4 |  |  |  |  | W | 0 | 0 | 0
Total LED Load | [8 empty] | 0
Sign Load 1 | Sign |  |  |  | W |  |  | 0
Sign Load 2 | Sign |  |  |  | W |  |  | 0
Sign Load 3 | Sign |  |  |  | W |  |  | 0
Sign Load 4 | Sign |  |  |  | W |  |  | 0
Sign Load 5 | Sign |  |  |  | W |  |  | 0
Total Sign Load | [8 empty] | 0
In-pavement RGL Fixture Load | L-852G |  |  |  | W | 0 | 0 | 0
In-pavement RGL Monitoring Device Load | [5 empty] | 0 | 0 | 0
Total In-pavement RGL Load | [8 empty] | 0
Elevated RGL Fixture Load | L-804 |  |  |  | W | 0 | 0 | 0
Elevated RGL Monitoring Device Load | [7 empty] | 0
Total Elevated RGL Load | [8 empty] | 0
Stop Bar In-pavement Load |  |  |  |  | W | 0 | 0 | 0
Stop Bar Elevated Fixture Load |  |  |  |  | W | 0 | 0 | 0
Stop Bar Sensor Load |  |  |  |  | W | 0 |  | 0
Stop Bar Elevated RGL Load | L-852G |  |  |  | W | 0 | 0 | 0
Stop Bar Monitoring Device Load | [7 empty] | 0
Total Stop Bar Load | [8 empty] | 0
Other Load 1 | [5 empty] | 0 | 0 | 0
Other Load 2 | [5 empty] | 0 | 0 | 0
Other Load 3 | [5 empty] | 0 | 0 | 0
Other Load 4 | [5 empty] | 0 | 0 | 0
Other Load 5 | [5 empty] | 0 | 0 | 0
Other Load 6 | [5 empty] | 0 | 0 | 0
Other Load 7 | [5 empty] | 0 | 0 | 0
Other Load 8 | [5 empty] | 0 | 0 | 0
Other Load 9 | [5 empty] | 0 | 0 | 0
Other Load 10 | [5 empty] | 0 | 0 | 0
Total Other Load | [8 empty] | 0
L-824 Wire Load | L-824 | Feet | AWG |  |  | 1 | 0 | 0
Total Calculated CCR Load | [8 empty] | 0
Desired Safety Factor |  | % Type in a percentage.
CCR Load with Safety Factor | 0 | VA
Next Largest CCR size | 0 | KW
Actual CCR Safety Factor | 0 | %
Recommended Tap Setting | 80 | % Tap
(Thyristor or SCR CCR only)
Do you want to export summary data to an overall CCR summary spreadsheet? | EXPORT | Clicking on this button exports this sheet to a new spreadsheet
CCR LOAD CALCULATOR ¦ © 2009-2014 ADB Airfield Solutions ¦ All Rights Reserved.

## variables (hidden)
2
output | frequency | architecture | units |  | awg | f | m | watts | xfmrloss |  | fixture | fixture2 | signtype
6.6 | 60Hz | Ferroresonant | Feet | AWG | 6 | 0.42 | 5.61 | 10 | 3 |  | L-850A | L-850A | L-858Y - Direction/Destination/Boundary |  | L-830-16 | 10/15 | 6.6A/6.6A | 70 | 3 / 4.5
20 | 50Hz | Thyristor | Meters | mm2 | 8 | 0.66 | 3.54 | 15 | 4.5 |  | L-850B | L-850B | L-858R - Mandatory |  | L-830-17 | 20/25 | 6.6A/6.6A | 70 | 6 / 7.5
|  | Other Manufacturer SCR | [5 empty] | 20 | 6 |  | L-850C | L-850C | L-858L - Runway/Taxiway Location |  | L-830-1 | 30/45 | 6.6A/6.6A | 80 | 6/9
signman | signsize |  | lamptype |  | 12 | 1.71 | 2.16 | 25 | 7.5 |  | L-850D | L-850D | L-858B - Runway Distance Remaining |  | L-830-2 | 30/45 | 20A/6.6A | 80 | 6/9
ADB | Size 1 | gendesc | Halogen |  | 16 | 4.35 | 1.37 | 30 | 6 |  | L-850E | L-850T |  |  | L-830-3 | 65 | 6.6A/6.6A | 80 | 13
| Size 2 | 1 Module | Fluorescent |  |  |  |  | 45 | 9 |  | L-850F | L-852A | signstyle |  | L-830-4 | 100 | 6.6A/6.6A | 85 | 15
lampwatt | Size 3 | 2 Module | LED |  | lamparch |  |  | 65 | 13 |  | L-852A | L-852B | Style 2 (4.8A - 6.6A) 3-step |  | L-830-5 | 100 | 20A/6.6A | 85 | 15
105 | Size 4 | 3 Module |  |  | Low VA |  |  | 100 | 15 |  | L-852B | L-852C | Style 3 (2.8A - 6.6A) 5-step |  | L-830-18 | 150 | 6.6A/6.6A | 85 | 22.5
| Size 5 | 4 Module | watts2 |  | Standard VA |  |  | 150 | 20 |  | L-852C | L-852D | Style 5 (5.5A only) |  | L-830-19 | 150 | 20A/20A | 85 | 22.5
monitor |  | 700 mm | 100 |  | 5.5A (Single-step) |  |  | 200 | 22.5 |  | L-852D | L-852J |  |  | L-830-6 | 200 | 6.6A/6.6A | 90 | 20
Monitored | pulsing | 900 mm |  |  | Fluorescent |  |  | 300 | 30 |  | L-852E | L-852K | otherdesc |  | L-830-7 | 200 | 20A/6.6A | 90 | 20
Un-Monitored | BRITE II Single Remote | 1100 mm | fixdesc |  | FAA LED |  |  | 500 | 50 |  | L-852F | L-852S | L-849A/C/E REIL with PA-4 |  | L-830-8 | 300 | 6.6A/20A | 90 | 30
| BRITE III (AGLAS) Single Remote | 1300 mm | L-852S |  | ICAO LED (Single Sided) (600 mm) |  |  | 1500 | 75 |  | L-852T | L-852T | L-849A/E LED REIL |  | L-830-9 | 300 | 20A/20A | 90 | 30
|  | 1500 mm | L-852G/S |  | ICAO LED (Dual Sided) (600 mm) | [5 empty] | L-860 | L-861 | L-849C LED REIL |  | L-830-10 | 300 | 6.6A/6.6A | 90 | 30
| Thyristor | 1700 mm |  |  | ICAO LED (Single Sided) (800 mm) | [5 empty] | L-860E | L-861E | 4-Box (L-880) Type B (Current Driven) 2-Lamp Optical Box |  | L-830-11 | 300 | 20A/6.6A | 90 | 30
| 10 | 1900 mm | irgldesc |  | ICAO LED (Dual Sided) (800 mm) |  | 2.5 |  | 5.61 |  | L-861 | L-861T | 4-Box (L-880) Type B (Current Driven) 3-Lamp Optical Box |  | L-830-12 | 500 | 6.6A/20A | 90 | 50
| 20 | 2100 mm | L-852G |  |  |  | 4 |  | 3.54 |  | L-861E | L-862 | 2-Box (L-881) Type B (Current Driven) 2-Lamp Optical Box |  | L-830-13 | 500 | 20A/20A | 90 | 50
| 30 | 2300 mm |  |  | sensor |  | 6 | 0.42 | 2.16 |  | L-861T | L-862E | 2-Box (L-881) Type B (Current Driven) 3-Lamp Optical Box |  | L-830-15 | 500 | 20A/6.6A | 90 | 50
| 40 | 2500 mm | ergldesc |  | Microwave |  | 8 | 0.66 |  |  | L-861SE |  | 4-Box (L-880) Type B (Current Driven) Single Channel PAPI
| 50 | 2700 mm | L-804 |  | Inductive Loop |  | 10 |  | 1.37 |  | L-862 |  | 2-Box (L-881) Type B (Current Driven) Single Channel PAPI
| 60 | 2900 mm |  |  |  |  | 12 | 1.71 |  |  | L-862E |  | 4-Box LED PAPI (L-880) (Current Driven) | 15
| 70 | 3300 mm |  |  | transform |  | 16 | 4.35 |  |  | L-862S |  | 2-Box LED PAPI (L-881) (Current Driven) | 20
| 80 | 3700 mm |  |  | 65 | 65 | awg |  | mm2 |  | Approach (UEL) |  | L-806 Wind Cone with PA-4 | 25
| 90 |  |  |  | 100 | 100 | 6 | 0.42 | 2.5 | 5.61 | Approach (PAR-56) |  | L-807 Wind Cone with PA-4
| 100 | inputvoltage |  |  | 150 | 150 | 8 | 0.66 | 4 | 3.54 | Approach (In-pavement) |  | L-806 LED Wind Cone Internally Lit (Current Driven)
|  | 208Vac |  |  | 200 | 200 | 12 | 1.71 | 6 | 2.16 |  |  | L-806 LED Wind Cone Externally Lit (Current Driven)
| yesno | 220Vac |  |  | 300 | 300 | 16 | 4.35 | 10 | 1.37 |  |  | L-807 LED Wind Cone Internally Lit (Current Driven)
| Yes | 230Vac |  |  | 500 | 500 | [6 empty] | L-807 LED Wind Cone Externally Lit (Current Driven)
| No | 240Vac |  |  | 300 (2) | 600
|  | 347Vac |  |  | 500 & 300 | 800 | [6 empty] | fpulsing
| ccrsteps | 380Vac |  |  | 500 (2) | 1000 | [6 empty] | Internal PCB (unmonitored only)
| 3-Step (4.8A-6.6A) | 400Vac | [10 empty] | BRITE II Dual Remote
| 5-Step (2.8A-6.6A) | 480Vac | [10 empty] | BRITE III Dual Remote (AGLAS)
| 5-Step (8.5A-20A) | 600Vac
| 1-Step (5.5A) | 2400Vac | [10 empty] | npulsing
BRITE II Dual Remote
BRITE III Dual Remote (AGLAS)

## SL Table (hidden)
type | architecture | style | Sign Size | watts | Modules | Transformer | Lamps | Power factor | load
Halogen | Low Va | 2 | 1 | 48 | 1 | 100 | 1 | 0.98 | 106
Halogen | Low Va | 2 | 1 | 48 | 2 | 200 | 2 | 0.99 | 155
Halogen | Low Va | 2 | 1 | 48 | 3 | 300 | 3 | 0.98 | 202
Halogen | Low Va | 2 | 1 | 48 | 4 | 300 | 4 | 0.99 | 250
Halogen | Low Va | 2 | 2 | 48 | 1 | 200 | 2 | 0.99 | 155
Halogen | Low Va | 2 | 2 | 48 | 2 | 300 | 4 | 0.99 | 250
Halogen | Low Va | 2 | 2 | 48 | 3 | 500 | 6 | 0.98 | 340
Halogen | Low Va | 2 | 2 | 48 | 4 | 300 (2) | 8 | 0.97 | 450
Halogen | Low Va | 2 | 3 | 48 | 1 | 200 | 2 | 0.99 | 155
Halogen | Low Va | 2 | 3 | 48 | 2 | 300 | 4 | 0.99 | 250
Halogen | Low Va | 2 | 3 | 48 | 3 | 500 | 6 | 0.98 | 340
Halogen | Low Va | 2 | 3 | 48 | 4 | 300 (2) | 8 | 0.97 | 450
Halogen | Low Va | 2 | 4 | 48 | 1 | 300 | 4 | 0.99 | 250
Halogen | Low Va | 2 | 5 | 48 | 1 | 200 | 2 | 0.99 | 155
Halogen | Low Va | 3 | 1 | 48 | 1 | 200 | 1 | 0.97 | 105
Halogen | Low Va | 3 | 1 | 48 | 2 | 300 | 2 | 0.98 | 145
Halogen | Low Va | 3 | 1 | 48 | 3 | 500 | 3 | 0.98 | 190
Halogen | Low Va | 3 | 1 | 48 | 4 | 500 | 4 | 0.98 | 233
Halogen | Low Va | 3 | 2 | 48 | 1 | 300 | 2 | 0.98 | 145
Halogen | Low Va | 3 | 2 | 48 | 2 | 500 | 4 | 0.98 | 233
Halogen | Low Va | 3 | 2 | 48 | 3 | 500 & 300 | 6 | 0.98 | 350
Halogen | Low Va | 3 | 2 | 48 | 4 | 500 (2) | 8 | 0.97 | 440
Halogen | Low Va | 3 | 3 | 48 | 1 | 300 | 2 | 0.98 | 145
Halogen | Low Va | 3 | 3 | 48 | 2 | 500 | 4 | 0.98 | 233
Halogen | Low Va | 3 | 3 | 48 | 3 | 500 & 300 | 6 | 0.98 | 350
Halogen | Low Va | 3 | 3 | 48 | 4 | 500 (2) | 8 | 0.97 | 440
Halogen | Low Va | 3 | 4 | 48 | 1 | 500 | 4 | 0.98 | 233
Halogen | Low Va | 3 | 5 | 48 | 1 | 300 | 2 | 0.98 | 145
Halogen | Low Va | 5 | 1 | 48 | 1 | 65 | 1 | 0.99 | 48
Halogen | Low Va | 5 | 1 | 48 | 2 | 100 | 2 | 0.99 | 96
Halogen | Low Va | 5 | 1 | 48 | 3 | 200 | 3 | 0.99 | 144
Halogen | Low Va | 5 | 1 | 48 | 4 | 200 | 4 | 0.99 | 192
Halogen | Low Va | 5 | 2 | 48 | 1 | 100 | 2 | 0.99 | 96
Halogen | Low Va | 5 | 2 | 48 | 2 | 200 | 4 | 0.99 | 192
Halogen | Low Va | 5 | 2 | 48 | 3 | 300 | 6 | 1 | 288
Halogen | Low Va | 5 | 2 | 48 | 4 | 500 | 8 | 0.98 | 384
Halogen | Low Va | 5 | 3 | 48 | 1 | 100 | 2 | 0.99 | 96
Halogen | Low Va | 5 | 3 | 48 | 2 | 200 | 4 | 0.99 | 192
Halogen | Low Va | 5 | 3 | 48 | 3 | 300 | 6 | 1 | 288
Halogen | Low Va | 5 | 3 | 48 | 4 | 500 | 8 | 0.98 | 384
Halogen | Low Va | 5 | 4 | 48 | 1 | 200 | 4 | 0.99 | 192
Halogen | Low Va | 5 | 5 | 48 | 1 | 100 | 2 | 0.99 | 96
Halogen | Standard Va | 2 | 1 | 48 | 1 | 30/45 | 1 | 0.59 | 104
Halogen | Standard Va | 2 | 1 | 48 | 2 | 100 | 2 | 0.46 | 222
Halogen | Standard Va | 2 | 1 | 48 | 3 | 100 | 3 | 0.52 | 302
Halogen | Standard Va | 2 | 1 | 48 | 4 | 200 | 4 | 0.52 | 319
Halogen | Standard Va | 2 | 2 | 48 | 1 | 100 | 2 | 0.46 | 222
Halogen | Standard Va | 2 | 2 | 48 | 2 | 200 | 4 | 0.52 | 319
Halogen | Standard Va | 2 | 2 | 48 | 3 | 300 | 6 | 0.48 | 460
Halogen | Standard Va | 2 | 2 | 48 | 4 | 300 | 8 | 0.53 | 570
Halogen | Standard Va | 2 | 3 | 48 | 1 | 100 | 2 | 0.46 | 222
Halogen | Standard Va | 2 | 3 | 48 | 2 | 200 | 4 | 0.52 | 319
Halogen | Standard Va | 2 | 3 | 48 | 3 | 300 | 6 | 0.48 | 460
Halogen | Standard Va | 2 | 3 | 48 | 4 | 300 | 8 | 0.53 | 570
Halogen | Standard Va | 2 | 4 | 48 | 1 | 200 | 4 | 0.52 | 319
Halogen | Standard Va | 2 | 5 | 48 | 1 | 100 | 2 | 0.46 | 222
Halogen | Standard Va | 3 | 1 | 48 | 1 | 100 | 1 | 0.21 | 231
Halogen | Standard Va | 3 | 1 | 48 | 2 | 200 | 2 | 0.32 | 316
Halogen | Standard Va | 3 | 1 | 48 | 3 | 300 | 3 | 0.24 | 641
Halogen | Standard Va | 3 | 1 | 48 | 4 | 500 | 4 | 0.31 | 652
Halogen | Standard Va | 3 | 2 | 48 | 1 | 200 | 2 | 0.32 | 316
Halogen | Standard Va | 3 | 2 | 48 | 2 | 300 | 4 | 0.21 | 652
Halogen | Standard Va | 3 | 2 | 48 | 3 | 500 | 6 | 0.23 | 910
Halogen | Standard Va | 3 | 2 | 48 | 4 | 300 (2) | 8 | 0.31 | 1304
Halogen | Standard Va | 3 | 3 | 48 | 1 | 200 | 2 | 0.32 | 316
Halogen | Standard Va | 3 | 3 | 48 | 2 | 300 | 4 | 0.21 | 652
Halogen | Standard Va | 3 | 3 | 48 | 3 | 500 | 6 | 0.23 | 910
Halogen | Standard Va | 3 | 3 | 48 | 4 | 300 (2) | 8 | 0.31 | 1304
Halogen | Standard Va | 3 | 4 | 48 | 1 | 500 | 4 | 0.31 | 652
Halogen | Standard Va | 3 | 5 | 48 | 1 | 300 | 2 | 0.32 | 316
Fluorescent | Fluorescent | 2 | 1 | 18 | 1 | 100 | 1 | 0.74 | 57
Fluorescent | Fluorescent | 2 | 1 | 18 | 2 | 200 | 2 | 0.58 | 119
Fluorescent | Fluorescent | 2 | 1 | 18 | 3 | 200 | 3 | 0.61 | 147
Fluorescent | Fluorescent | 2 | 1 | 18 | 4 | 300 | 4 | 0.62 | 178
Fluorescent | Fluorescent | 2 | 2 | 18 | 1 | 200 | 2 | 0.58 | 119
Fluorescent | Fluorescent | 2 | 2 | 18 | 2 | 300 | 4 | 0.62 | 178
Fluorescent | Fluorescent | 2 | 2 | 18 | 3 | 300 | 6 | 0.64 | 229
Fluorescent | Fluorescent | 2 | 2 | 18 | 4 | 300 (2) | 8 | 0.55 | 380
Fluorescent | Fluorescent | 2 | 3 | 18 | 1 | 200 | 2 | 0.58 | 119
Fluorescent | Fluorescent | 2 | 3 | 18 | 2 | 300 | 4 | 0.62 | 178
Fluorescent | Fluorescent | 2 | 3 | 18 | 3 | 300 | 6 | 0.64 | 229
Fluorescent | Fluorescent | 2 | 3 | 18 | 4 | 300 (2) | 8 | 0.55 | 380
Fluorescent | Fluorescent | 2 | 4 | 18 | 1 | 300 | 4 | 0.62 | 178
Fluorescent | Fluorescent | 2 | 5 | 18 | 1 | 200 | 2 | 0.58 | 119
Fluorescent | Fluorescent | 3 | 1 | 18 | 1 | 100 | 1 | 0.6 | 79
Fluorescent | Fluorescent | 3 | 1 | 18 | 2 | 200 | 2 | 0.5 | 157
Fluorescent | Fluorescent | 3 | 1 | 18 | 3 | 300 | 3 | 0.49 | 195
Fluorescent | Fluorescent | 3 | 1 | 18 | 4 | 300 | 4 | 0.51 | 231
Fluorescent | Fluorescent | 3 | 2 | 18 | 1 | 200 | 2 | 0.5 | 157
Fluorescent | Fluorescent | 3 | 2 | 18 | 2 | 300 | 4 | 0.51 | 231
Fluorescent | Fluorescent | 3 | 2 | 18 | 3 | 500 | 6 | 0.46 | 350
Fluorescent | Fluorescent | 3 | 2 | 18 | 4 | 300 (2) | 8 | 0.44 | 480
Fluorescent | Fluorescent | 3 | 3 | 18 | 1 | 200 | 2 | 0.5 | 157
Fluorescent | Fluorescent | 3 | 3 | 18 | 2 | 300 | 4 | 0.51 | 231
Fluorescent | Fluorescent | 3 | 3 | 18 | 3 | 500 | 6 | 0.46 | 350
Fluorescent | Fluorescent | 3 | 3 | 18 | 4 | 300 (2) | 8 | 0.44 | 480
Fluorescent | Fluorescent | 3 | 4 | 18 | 1 | 300 | 4 | 0.51 | 231
Fluorescent | Fluorescent | 3 | 5 | 18 | 1 | 200 | 2 | 0.5 | 157
Fluorescent | Fluorescent | 5 | 1 | 18 | 1 | 100 | 1 | 0.8 | 48
Fluorescent | Fluorescent | 5 | 1 | 18 | 2 | 200 | 2 | 0.69 | 99
Fluorescent | Fluorescent | 5 | 1 | 18 | 3 | 200 | 3 | 0.72 | 122
Fluorescent | Fluorescent | 5 | 1 | 18 | 4 | 300 | 4 | 0.73 | 148
Fluorescent | Fluorescent | 5 | 2 | 18 | 1 | 200 | 2 | 0.69 | 99
Fluorescent | Fluorescent | 5 | 2 | 18 | 2 | 300 | 4 | 0.73 | 148
Fluorescent | Fluorescent | 5 | 2 | 18 | 3 | 300 | 6 | 0.75 | 190
Fluorescent | Fluorescent | 5 | 2 | 18 | 4 | 300 (2) | 8 | 0.66 | 317
Fluorescent | Fluorescent | 5 | 3 | 18 | 1 | 200 | 2 | 0.69 | 99
Fluorescent | Fluorescent | 5 | 3 | 18 | 2 | 300 | 4 | 0.73 | 148
Fluorescent | Fluorescent | 5 | 3 | 18 | 3 | 300 | 6 | 0.75 | 190
Fluorescent | Fluorescent | 5 | 3 | 18 | 4 | 300 (2) | 8 | 0.66 | 317
Fluorescent | Fluorescent | 5 | 4 | 18 | 1 | 300 | 4 | 0.73 | 148
Fluorescent | Fluorescent | 5 | 5 | 18 | 1 | 200 | 2 | 0.69 | 99
LED | FAA LED | 2 | 1 |  | 1 | 65 |  | 0.83 | 85
LED | FAA LED | 2 | 1 |  | 2 | 100 |  | 0.83 | 95
LED | FAA LED | 2 | 1 |  | 3 | 100 |  | 0.88 | 95
LED | FAA LED | 2 | 1 |  | 4 | 100 |  | 0.91 | 95
LED | FAA LED | 2 | 2 |  | 1 | 65 |  | 0.88 | 90
LED | FAA LED | 2 | 2 |  | 2 | 100 |  | 0.88 | 95
LED | FAA LED | 2 | 2 |  | 3 | 100 |  | 0.91 | 100
LED | FAA LED | 2 | 2 |  | 4 | 100 |  | 0.91 | 100
LED | FAA LED | 2 | 3 |  | 1 | 100 |  | 0.83 | 95
LED | FAA LED | 2 | 3 |  | 2 | 100 |  | 0.91 | 95
LED | FAA LED | 2 | 3 |  | 3 | 100 |  | 0.91 | 100
LED | FAA LED | 2 | 3 |  | 4 | 150 |  | 0.88 | 115
LED | FAA LED | 2 | 4 |  | 1 | 100 |  | 0.84 | 95
LED | FAA LED | 2 | 5 |  | 1 | 100 |  | 0.83 | 95
LED | FAA LED | 3 | 1 |  | 1 | 100 |  | 0.88 | 75
LED | FAA LED | 3 | 1 |  | 2 | 150 |  | 0.88 | 95
LED | FAA LED | 3 | 1 |  | 3 | 150 |  | 0.88 | 95
LED | FAA LED | 3 | 1 |  | 4 | 150 |  | 0.9 | 100
LED | FAA LED | 3 | 2 |  | 1 | 150 |  | 0.88 | 90
LED | FAA LED | 3 | 2 |  | 2 | 150 |  | 0.9 | 95
LED | FAA LED | 3 | 2 |  | 3 | 150 |  | 0.83 | 100
LED | FAA LED | 3 | 2 |  | 4 | 150 |  | 0.83 | 100
LED | FAA LED | 3 | 3 |  | 1 | 150 |  | 0.88 | 95
LED | FAA LED | 3 | 3 |  | 2 | 150 |  | 0.9 | 100
LED | FAA LED | 3 | 3 |  | 3 | 150 |  | 0.83 | 100
LED | FAA LED | 3 | 3 |  | 4 | 200 |  | 0.85 | 115
LED | FAA LED | 3 | 4 |  | 1 | 150 |  | 0.88 | 95
LED | FAA LED | 3 | 5 |  | 1 | 150 |  | 0.83 | 95
LED | FAA LED | 5 | 1 |  | 1 | 65 |  | 0.84 | 75
LED | FAA LED | 5 | 1 |  | 2 | 65 |  | 0.84 | 85
LED | FAA LED | 5 | 1 |  | 3 | 100 |  | 0.88 | 85
LED | FAA LED | 5 | 1 |  | 4 | 100 |  | 0.88 | 95
LED | FAA LED | 5 | 2 |  | 1 | 65 |  | 0.92 | 75
LED | FAA LED | 5 | 2 |  | 2 | 100 |  | 0.89 | 85
LED | FAA LED | 5 | 2 |  | 3 | 100 |  | 0.9 | 100
LED | FAA LED | 5 | 2 |  | 4 | 100 |  | 0.9 | 100
LED | FAA LED | 5 | 3 |  | 1 | 65 |  | 0.84 | 85
LED | FAA LED | 5 | 3 |  | 2 | 100 |  | 0.88 | 95
LED | FAA LED | 5 | 3 |  | 3 | 100 |  | 0.92 | 100
LED | FAA LED | 5 | 3 |  | 4 | 100 |  | 0.92 | 110
LED | FAA LED | 5 | 4 |  | 1 | 65 |  | 0.83 | 85
LED | FAA LED | 5 | 5 |  | 1 | 65 |  | 0.92 | 85
LED | ICAO LED (Single Sided) (600mm) | 2 | 1 |  | 1 | 65 |  | 0.83 | 85
LED | ICAO LED (Single Sided) (600mm) | 2 | 1 |  | 2 | 100 |  | 0.83 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 1 |  | 3 | 100 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 1 |  | 4 | 100 |  | 0.91 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 2 |  | 1 | 65 |  | 0.88 | 90
LED | ICAO LED (Single Sided) (600mm) | 2 | 2 |  | 2 | 100 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 2 |  | 3 | 100 |  | 0.91 | 100
LED | ICAO LED (Single Sided) (600mm) | 2 | 2 |  | 4 | 100 |  | 0.91 | 100
LED | ICAO LED (Single Sided) (600mm) | 2 | 3 |  | 1 | 100 |  | 0.83 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 3 |  | 2 | 100 |  | 0.91 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 3 |  | 3 | 100 |  | 0.91 | 100
LED | ICAO LED (Single Sided) (600mm) | 2 | 3 |  | 4 | 150 |  | 0.88 | 115
LED | ICAO LED (Single Sided) (600mm) | 2 | 4 |  | 1 | 100 |  | 0.84 | 95
LED | ICAO LED (Single Sided) (600mm) | 2 | 5 |  | 1 | 100 |  | 0.83 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 1 |  | 1 | 100 |  | 0.88 | 75
LED | ICAO LED (Single Sided) (600mm) | 3 | 1 |  | 2 | 150 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 1 |  | 3 | 150 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 1 |  | 4 | 150 |  | 0.9 | 100
LED | ICAO LED (Single Sided) (600mm) | 3 | 2 |  | 1 | 150 |  | 0.88 | 90
LED | ICAO LED (Single Sided) (600mm) | 3 | 2 |  | 2 | 150 |  | 0.9 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 2 |  | 3 | 150 |  | 0.83 | 100
LED | ICAO LED (Single Sided) (600mm) | 3 | 2 |  | 4 | 150 |  | 0.83 | 100
LED | ICAO LED (Single Sided) (600mm) | 3 | 3 |  | 1 | 150 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 3 |  | 2 | 150 |  | 0.9 | 100
LED | ICAO LED (Single Sided) (600mm) | 3 | 3 |  | 3 | 150 |  | 0.83 | 100
LED | ICAO LED (Single Sided) (600mm) | 3 | 3 |  | 4 | 200 |  | 0.85 | 115
LED | ICAO LED (Single Sided) (600mm) | 3 | 4 |  | 1 | 150 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 3 | 5 |  | 1 | 150 |  | 0.83 | 95
LED | ICAO LED (Single Sided) (600mm) | 5 | 1 |  | 1 | 65 |  | 0.84 | 75
LED | ICAO LED (Single Sided) (600mm) | 5 | 1 |  | 2 | 65 |  | 0.84 | 85
LED | ICAO LED (Single Sided) (600mm) | 5 | 1 |  | 3 | 100 |  | 0.88 | 85
LED | ICAO LED (Single Sided) (600mm) | 5 | 1 |  | 4 | 100 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 5 | 2 |  | 1 | 65 |  | 0.92 | 75
LED | ICAO LED (Single Sided) (600mm) | 5 | 2 |  | 2 | 100 |  | 0.89 | 85
LED | ICAO LED (Single Sided) (600mm) | 5 | 2 |  | 3 | 100 |  | 0.9 | 100
LED | ICAO LED (Single Sided) (600mm) | 5 | 2 |  | 4 | 100 |  | 0.9 | 100
LED | ICAO LED (Single Sided) (600mm) | 5 | 3 |  | 1 | 65 |  | 0.84 | 85
LED | ICAO LED (Single Sided) (600mm) | 5 | 3 |  | 2 | 100 |  | 0.88 | 95
LED | ICAO LED (Single Sided) (600mm) | 5 | 3 |  | 3 | 100 |  | 0.92 | 100
LED | ICAO LED (Single Sided) (600mm) | 5 | 3 |  | 4 | 100 |  | 0.92 | 110
LED | ICAO LED (Single Sided) (600mm) | 5 | 4 |  | 1 | 65 |  | 0.83 | 85
LED | ICAO LED (Single Sided) (600mm) | 5 | 5 |  | 1 | 65 |  | 0.92 | 85